## IEEE 14 Bus Data
Appendix A: IEEE 14-Bus Test System Data
BUS DATA
Bus Number | [10 empty] | Voltage Base (kV) | [16 empty] | V0 (PU) | [10 empty] | θ0 (rad)
1 | [10 empty] | 69 | [16 empty] | 1 | [10 empty] | 0
2 | [10 empty] | 69 | [16 empty] | 1 | [10 empty] | 0
3 | [10 empty] | 69 | [16 empty] | 1 | [10 empty] | 0
4 | [10 empty] | 69 | [16 empty] | 1 | [10 empty] | 0
5 | [10 empty] | 69 | [16 empty] | 1 | [10 empty] | 0
6 | [10 empty] | 13.8 | [16 empty] | 1 | [10 empty] | 0
7 | [10 empty] | 13.8 | [16 empty] | 1 | [10 empty] | 0
8 | [10 empty] | 18 | [16 empty] | 1 | [10 empty] | 0
9 | [10 empty] | 13.8 | [16 empty] | 1 | [10 empty] | 0
10 | [10 empty] | 13.8 | [16 empty] | 1 | [10 empty] | 0
11 | [10 empty] | 13.8 | [16 empty] | 1 | [10 empty] | 0
12 | [10 empty] | 13.8 | [16 empty] | 1 | [10 empty] | 0
13 | [10 empty] | 13.8 | [16 empty] | 1 | [10 empty] | 0
14 | [10 empty] | 13.8 | [16 empty] | 1 | [10 empty] | 0
SLACK GENERATOR DATA
Bus Number |  |  |  | Power rating (MVA) | [7 empty] | Voltage rating (kV) |  |  |  |  | V0 (Pu) |  |  | θ0 (Pu) |  |  |  | Q max (Pu) | [5 empty] | Q min (Pu) | [6 empty] | V max (Pu) | [5 empty] | V min (Pu)
1 |  |  |  | 100 | [7 empty] | 69 |  |  |  |  | 1.06 |  |  | 0 |  |  |  | 9.9 | [5 empty] | -9.9 | [6 empty] | 1.061 | [5 empty] | 0.8
PV GENERATOR DATA
Bus Number |  |  | Power Rating (MVA) | [6 empty] | Voltage Rating (kV) | [5 empty] | Active Power (Pu) |  |  |  |  | V0 (Pu) |  |  |  |  | Q max (Pu) | [6 empty] | Q min (Pu) |  |  |  |  | V max (Pu) | [5 empty] | V min (Pu)
2 |  |  | 100 | [6 empty] | 69 | [5 empty] | 0.4 |  |  |  |  | 1.045 |  |  |  |  | 0.5 | [6 empty] | -0.4 |  |  |  |  | 1.0451 | [5 empty] | 0.8
6 |  |  | 100 | [6 empty] | 13.8 | [5 empty] | 0 |  |  |  |  | 1.07 |  |  |  |  | 0.24 | [6 empty] | -0.06 |  |  |  |  | 1.0701 | [5 empty] | 0.6
3 |  |  | 100 | [6 empty] | 69 | [5 empty] | 0 |  |  |  |  | 1.01 |  |  |  |  | 0.4 | [6 empty] | 0 |  |  |  |  | 1.0101 | [5 empty] | 0.6
8 |  |  | 100 | [6 empty] | 18 | [5 empty] | 0 |  |  |  |  | 1.09 |  |  |  |  | 0.2517 | [6 empty] | -0.06 |  |  |  |  | 1.0901 | [5 empty] | 0.6
TRANSFORMER DATA
From Bus | To Bus |  |  |  |  | Power Rating (MVA) | [6 empty] | Voltage Rating (kV) |  |  |  | Frequency Rating (Hz) |  |  |  |  | Voltage Ratio (kV/kV) | [6 empty] | R (Pu) | [5 empty] | X (Pu) |  |  |  |  | Fix Tap Ratio (Pu/Pu)
5 | 6 |  |  |  |  | 100 | [6 empty] | 69 |  |  |  | 60 |  |  |  |  | 5 | [6 empty] | 0 | [5 empty] | 0.25202 |  |  |  |  | 0.932
4 | 9 |  |  |  |  | 100 | [6 empty] | 69 |  |  |  | 60 |  |  |  |  | 5 | [6 empty] | 0 | [5 empty] | 0.55618 |  |  |  |  | 0.969
4 | 7 |  |  |  |  | 100 | [6 empty] | 69 |  |  |  | 60 |  |  |  |  | 5 | [6 empty] | 0 | [5 empty] | 0.20912 |  |  |  |  | 0.978
8 | 7 |  |  |  |  | 100 | [6 empty] | 18 |  |  |  | 60 |  |  |  |  | 1.3043 | [6 empty] | 0 | [5 empty] | 0.17615 |  |  |  |  | 0
BRANCH DATA
From Bus |  | To Bus | [5 empty] | Power Rating (MVA) | [5 empty] | Voltage Rating (kV) |  |  |  |  | Frequency Rating (Hz) | [10 empty] | R (Pu) | [6 empty] | X (Pu) | [5 empty] | B(Pu) | [5 empty] | R(ohm/km) | X(ohm/km) | B(ohm/km) |  | C(ohm/km)
2 |  | 5 | [5 empty] | 100 | [5 empty] | 69 |  |  |  |  | 60 | [10 empty] | 0.05695 | [6 empty] | 0.17388 | [5 empty] | 0.034 | [5 empty] | 2.7114 | 8.2784 | 1.6187 |  | 610.265
6 |  | 12 | [5 empty] | 100 | [5 empty] | 13.8 |  |  |  |  | 60 | [10 empty] | 0.12291 | [6 empty] | 0.25581 | [5 empty] | 0 | [5 empty] | 0.23407 | 0.48716 | 0 |  | 0
12 |  | 13 | [5 empty] | 100 | [5 empty] | 13.8 |  |  |  |  | 60 | [10 empty] | 0.22092 | [6 empty] | 0.19988 | [5 empty] | 0 | [5 empty] | 0.42072 | 0.38065 | 0 |  | 0
6 |  | 13 | [5 empty] | 100 | [5 empty] | 13.8 |  |  |  |  | 60 | [10 empty] | 0.06615 | [6 empty] | 0.13027 | [5 empty] | 0 | [5 empty] | 0.12598 | 0.24809 | 0 |  | 0
6 |  | 11 | [5 empty] | 100 | [5 empty] | 13.8 |  |  |  |  | 60 | [10 empty] | 0.09498 | [6 empty] | 0.1989 | [5 empty] | 0 | [5 empty] | 0.18088 | 0.37879 | 0 |  | 0
11 |  | 10 | [5 empty] | 100 | [5 empty] | 13.8 |  |  |  |  | 60 | [10 empty] | 0.08205 | [6 empty] | 0.19207 | [5 empty] | 0 | [5 empty] | 0.15626 | 0.36578 | 0 |  | 0
9 |  | 10 | [5 empty] | 100 | [5 empty] | 13.8 |  |  |  |  | 60 | [10 empty] | 0.03181 | [6 empty] | 0.0845 | [5 empty] | 0 | [5 empty] | 0.060579 | 0.16092 | 0 |  | 0
9 |  | 14 | [5 empty] | 100 | [5 empty] | 13.8 |  |  |  |  | 60 | [10 empty] | 0.12711 | [6 empty] | 0.27038 | [5 empty] | 0 | [5 empty] | 0.24207 | 0.51491 | 0 |  | 0
14 |  | 13 | [5 empty] | 100 | [5 empty] | 13.8 |  |  |  |  | 60 | [10 empty] | 0.17093 | [6 empty] | 0.34802 | [5 empty] | 0 | [5 empty] | 0.32552 | 0.66277 | 0 |  | 0
7 |  | 9 | [5 empty] | 100 | [5 empty] | 13.8 |  |  |  |  | 60 | [10 empty] | 0 | [6 empty] | 0.11001 | [5 empty] | 0 | [5 empty] | 0 | 0.2095 | 0 |  | 0
1 |  | 2 | [5 empty] | 100 | [5 empty] | 69 |  |  |  |  | 60 | [10 empty] | 0.01938 | [6 empty] | 0.05917 | [5 empty] | 0.0528 | [5 empty] | 0.92268 | 2.8171 | 2.5138 |  | 947.7056
3 |  | 2 | [5 empty] | 100 | [5 empty] | 69 |  |  |  |  | 60 | [10 empty] | 0.04699 | [6 empty] | 0.19797 | [5 empty] | 0.0438 | [5 empty] | 2.2372 | 9.4254 | 2.0853 |  | 786.1649
3 |  | 4 | [5 empty] | 100 | [5 empty] | 69 |  |  |  |  | 60 | [10 empty] | 0.06701 | [6 empty] | 0.17103 | [5 empty] | 0.0346 | [5 empty] | 3.1903 | 8.1427 | 1.6473 |  | 621.0344
1 |  | 5 | [5 empty] | 100 | [5 empty] | 69 |  |  |  |  | 60 | [10 empty] | 0.05403 | [6 empty] | 0.22304 | [5 empty] | 0.0492 | [5 empty] | 2.5724 | 10.6189 | 2.3424 |  | 883.0893
5 |  | 4 | [5 empty] | 100 | [5 empty] | 69 |  |  |  |  | 60 | [10 empty] | 0.01335 | [6 empty] | 0.04211 | [5 empty] | 0.0128 | [5 empty] | 0.63559 | 2.0049 | 0.60941 |  | 229.7468
2 |  | 4 | [5 empty] | 100 | [5 empty] | 69 |  |  |  |  | 60 | [10 empty] | 0.05811 | [6 empty] | 0.17632 | [5 empty] | 0.0374 | [5 empty] | 2.7666 | 8.3946 | 1.7806 |  | 671.2915
5 |  | 6 | [5 empty] | 100 | [5 empty] | 69 |  |  |  |  | 60 | [10 empty] | 0 | [6 empty] | 0.25202 | [5 empty] | 0 | [5 empty] | 0 | 11.9987 | 0 |  | 0
4 |  | 9 | [5 empty] | 100 | [5 empty] | 69 |  |  |  |  | 60 | [10 empty] | 0 | [6 empty] | 0.55618 | [5 empty] | 0 | [5 empty] | 0 | 26.4797 | 0 |  | 0
4 |  | 7 | [5 empty] | 100 | [5 empty] | 69 |  |  |  |  | 60 | [10 empty] | 0 | [6 empty] | 0.20912 | [5 empty] | 0 | [5 empty] | 0 | 9.9562 | 0 |  | 0
8 |  | 7 | [5 empty] | 100 | [5 empty] | 18 |  |  |  |  | 60 | [10 empty] | 0 | [6 empty] | 0.17615 | [5 empty] | 0 | [5 empty] | 0 | 8.3865 | 0 |  | 0
PQ LOAD DATA
Bus Number |  |  |  | Power Rating (MVA) | [8 empty] | Voltage rating (kv) |  |  |  |  | Active Power (Pu) | [6 empty] | Reactive Power (Pu) | [11 empty] | V max (Pu) | [5 empty] | V min (Pu)
11 |  |  |  | 100 | [8 empty] | 13.8 |  |  |  |  | 0.035 | [6 empty] | 0.018 | [11 empty] | 1.2 | [5 empty] | 0.6
13 |  |  |  | 100 | [8 empty] | 13.8 |  |  |  |  | 0.135 | [6 empty] | 0.058 | [11 empty] | 1.2 | [5 empty] | 0.6
3 |  |  |  | 100 | [8 empty] | 69 |  |  |  |  | 0.942 | [6 empty] | 0.19 | [11 empty] | 1.5 | [5 empty] | 0.8
5 |  |  |  | 100 | [8 empty] | 69 |  |  |  |  | 0.076 | [6 empty] | 0.016 | [11 empty] | 1.2 | [5 empty] | 0.6
2 |  |  |  | 100 | [8 empty] | 69 |  |  |  |  | 0.217 | [6 empty] | 0.127 | [11 empty] | 1.2 | [5 empty] | 0.8
6 |  |  |  | 100 | [8 empty] | 13.8 |  |  |  |  | 0.112 | [6 empty] | 0.075 | [11 empty] | 1.5 | [5 empty] | 0.6
4 |  |  |  | 100 | [8 empty] | 69 |  |  |  |  | 0.478 | [6 empty] | 0.04 | [11 empty] | 1.2 | [5 empty] | 0.6
14 |  |  |  | 100 | [8 empty] | 13.8 |  |  |  |  | 0.149 | [6 empty] | 0.05 | [11 empty] | 1.2 | [5 empty] | 0.5
12 |  |  |  | 100 | [8 empty] | 13.8 |  |  |  |  | 0.061 | [6 empty] | 0.016 | [11 empty] | 1.2 | [5 empty] | 0.6
10 |  |  |  | 100 | [8 empty] | 13.8 |  |  |  |  | 0.09 | [6 empty] | 0.058 | [11 empty] | 1.2 | [5 empty] | 0.6
9 |  |  |  | 100 | [8 empty] | 13.8 |  |  |  |  | 0.295 | [6 empty] | 0.166 | [11 empty] | 1.2 | [5 empty] | 0.6
SYNCHRONOUS MACHINES DATA
Bus Number | Power Rating (MVA) | [5 empty] | Voltag e rating (kV) |  | Frequency rating (Hz) |  |  |  |  | Machine Model |  | XL (Pu) |  |  | ra (Pu) |  |  |  | Xd (Pu) |  |  |  | X'd (Pu) |  |  |  |  | X''d (Pu) |  |  |  | T'd0 (s) |  |  | T''d0 (s) |  | Xq (Pu) |  |  |  | X'q (Pu) |  |  | X''q (Pu) |  | T'q0 (s) | T''q0 (s) |  | M = 2H (kWs/kVA) |  | Damping coefficient
1 | 615 | [5 empty] | 69 |  | 60 |  |  |  |  | 5.2 |  | 0.2396 |  |  | 0 |  |  |  | 0.8979 |  |  |  | 0.6 |  |  |  |  | 0.23 |  |  |  | 7.4 |  |  | 0.03 |  | 0.646 |  |  |  | 0.646 |  |  | 0.4 |  | 0 | 0.033 |  | 10.296 |  | 2
3 | 60 | [5 empty] | 69 |  | 60 |  |  |  |  | 6 |  | 0 |  |  | 0.0031 |  |  |  | 1.05 |  |  |  | 0.185 |  |  |  |  | 0.13 |  |  |  | 6.1 |  |  | 0.04 |  | 0.98 |  |  |  | 0.36 |  |  | 0.13 |  | 0.3 | 0.099 |  | 13.08 |  | 2
2 | 60 | [5 empty] | 69 |  | 60 |  |  |  |  | 6 |  | 0 |  |  | 0.0031 |  |  |  | 1.05 |  |  |  | 0.185 |  |  |  |  | 0.13 |  |  |  | 6.1 |  |  | 0.04 |  | 0.98 |  |  |  | 0.36 |  |  | 0.13 |  | 0.3 | 0.099 |  | 13.08 |  | 2
8 | 25 | [5 empty] | 18 |  | 60 |  |  |  |  | 6 |  | 0.134 |  |  | 0.0014 |  |  |  | 1.25 |  |  |  | 0.232 |  |  |  |  | 0.12 |  |  |  | 4.75 |  |  | 0.06 |  | 1.22 |  |  |  | 0.715 |  |  | 0.12 |  | 1.5 | 0.21 |  | 10.12 |  | 2
6 | 25 | [5 empty] | 13.8 |  | 60 |  |  |  |  | 6 |  | 0.134 |  |  | 0.0014 |  |  |  | 1.25 |  |  |  | 0.232 |  |  |  |  | 0.12 |  |  |  | 4.75 |  |  | 0.06 |  | 1.22 |  |  |  | 0.715 |  |  | 0.12 |  | 1.5 | 0.21 |  | 10.12 |  | 2
TURBINE GOVERNOR DATA
Generator number | [12 empty] | Governor Type | [6 empty] | ωref0 (Pu) | [10 empty] | R (Pu) | [7 empty] | Tmax (Pu) | [7 empty] | Tmin (Pu) |  |  |  |  | T2 (s) |  | T1 (s)
3 | [12 empty] | 2 | [6 empty] | 1 | [10 empty] | 0.05 | [7 empty] | 1.2 | [7 empty] | 0.3 |  |  |  |  | 0.1 |  | 0.45
1 | [12 empty] | 2 | [6 empty] | 1 | [10 empty] | 0.05 | [7 empty] | 1.2 | [7 empty] | 0.3 |  |  |  |  | 0.1 |  | 0.45
EXCITER SYSTEM DATA
Generator Number |  |  |  |  | Exciter Type |  |  |  | Vr Max (Pu) | [5 empty] | Vr Min (Pu) |  |  | Ka (Pu/Pu) |  |  |  | Ta (s) |  |  |  | Kf (Pu/Pu) | [7 empty] | Tf (s) |  |  |  | Te (s) |  |  |  | Tr (s) |  |  |  | Ae-1st Ceiling coefficient | [5 empty] | Be-2nd Ceiling Coefficient
1 |  |  |  |  | 2 |  |  |  | 7.32 | [5 empty] | 0 |  |  | 200 |  |  |  | 0.02 |  |  |  | 0.002 | [7 empty] | 1 |  |  |  | 0.2 |  |  |  | 0.001 |  |  |  | 0.0006 | [5 empty] | 0.9
3 |  |  |  |  | 2 |  |  |  | 4.38 | [5 empty] | 0 |  |  | 20 |  |  |  | 0.02 |  |  |  | 0.001 | [7 empty] | 1 |  |  |  | 1.98 |  |  |  | 0.001 |  |  |  | 0.0006 | [5 empty] | 0.9
2 |  |  |  |  | 2 |  |  |  | 4.38 | [5 empty] | 0 |  |  | 20 |  |  |  | 0.02 |  |  |  | 0.001 | [7 empty] | 1 |  |  |  | 1.98 |  |  |  | 0.001 |  |  |  | 0.0006 | [5 empty] | 0.9
4 |  |  |  |  | 2 |  |  |  | 6.81 | [5 empty] | 1.395 |  |  | 20 |  |  |  | 0.02 |  |  |  | 0.001 | [7 empty] | 1 |  |  |  | 0.7 |  |  |  | 0.001 |  |  |  | 0.0006 | [5 empty] | 0.9
5 |  |  |  |  | 2 |  |  |  | 6.81 | [5 empty] | 1.395 |  |  | 20 |  |  |  | 0.02 |  |  |  | 0.001 | [7 empty] | 1 |  |  |  | 0.7 |  |  |  | 0.001 |  |  |  | 0.0006 | [5 empty] | 0.9
92

## Loadflow Results
Iteration data
Iterations: | 6
Mismatch: | 2e-05
From | To | P Loss | Q Loss | P Imp | Q Imp | P Gen | Q Gen | P Load | Q Load | Gen. Cost | Qc Shunt | Ql Shunt | Q Comp | Iron Losses
Area/Zone | Area/Zone | MW | MVar | MW | MVar | MW | MVar | MW | MVar | Curr. Units | MVar | MVar | MVar | MW
Network |  | 13.501 | 27.972 | 232.501 | -15.762 | 272.501 | 33.032 | 259 | 5.06 | 0 | 0 | 0 | 0 | 0
Area 1 |  | 13.501 | 27.972 | 0 | 0 | 272.501 | 33.032 | 259 | 5.06 | 0 | 0 | 0 | 0 | 0
Zone 1 |  | 13.501 | 27.972 | 0 | 0 | 272.501 | 33.032 | 259 | 5.06 | 0 | 0 | 0 | 0 | 0
Un |  | P Loss Line | Q Loss Line | P Loss Transformer | Q Loss Transformer
kV |  | MW | MVar | MW | MVar
13.8 |  | 0.588 | 2.721 | 0 | 0
18 |  | 0 | 0 | 0 | 0.89
69 |  | 12.913 | 16.727 | 0 | 7.635
ID | Node | U | u | Angle U | P Load | Q Load | P Gen | Q Gen | Q Shunt | dPL/dPG | dPL/dQG | DUfeed | Description | Zone | Area | Partial | Feeder
| Name | kV | % | ° | MW | MVar | MW | MVar | MVar | [5 empty] | Network
174095 | BUS-2 | 72.105 | 104.5 | -5 | 21.7 | 12.7 | 40 | 48.794 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174092 | BUS-1 | 73.14 | 106 | 0 | 0 | 15.762 | 232.501 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174089 | BUS-5 | 70.222 | 101.77 | -8.7 | 7.6 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174086 | BUS-4 | 69.715 | 101.04 | -10.2 | 47.8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174083 | BUS-8 | 19.224 | 106.8 | -13.5 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174080 | BUS-6 | 14.05 | 101.81 | -14.7 | 11.2 | 7.5 | 0 | 24 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174101 | BUS-7 | 14.192 | 102.84 | -13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174098 | BUS-3 | 69.69 | 101 | -12.8 | 94.2 | 19 | 0 | 28.34 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174062 | BUS-13 | 13.764 | 99.74 | -15.7 | 13.5 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174077 | BUS-10 | 13.767 | 99.76 | -15.5 | 9 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174074 | BUS-11 | 13.857 | 100.41 | -15.3 | 3.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174071 | BUS-9 | 13.837 | 100.26 | -15.3 | 29.5 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174068 | BUS-14 | 13.543 | 98.14 | -16.6 | 14.9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174065 | BUS-12 | 13.833 | 100.24 | -15.7 | 6.1 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
ID | Node | Element | Type | P | Q | I | Angle I | Loading | Scaling P | Scaling Q | P Loss | Q Loss | P Fe | P Comp | Q Comp | Tap | Ratio | Sens. Xser | Teta | Overlap | Margin | B tot | X tot | U series | Ang. U series | I shunt | Ang. I shunt | P exch | Q exch series | Q exch shunt | Slip | Torque | UR | Ang. UR | PR | QR | U TieLine | U LineLoad | P LineLoad | Q LineLoad | ON | Description | Zone | Area
| Name | Name |  | MW | MVar | kA | ° | % |  |  | MW | MVar | MW | MW | MVar |  |  | %/Ohm | ° | ° | ° | mS | Ohm | kV | ° | kA | ° | MW | MVar | MVar |  | Nm | V | ° | kW | kVar | % | kV | MW | MVar
174366 | BUS-5 | TL_5-4 | Line | 62.522 | -1.906 | 0.514 | -7 | 0 |  |  | 0.504 | 0.2737 |  | 0 | 0 |  |  | %/Ohm: 0
174361 | BUS-1 | TL_1-5 | Line | 75.355 | 4.704 | 0.596 | -3.6 | 0 |  |  | 2.7573 | 6.0706 |  | 0 | 0 |  |  | %/Ohm: 0
174361 | BUS-5 | TL_1-5 | Line | -72.598 | 1.366 | 0.597 | 172.3 | 0 |  |  | 2.7573 | 6.0706 |  | 0 | 0 |  |  | %/Ohm: 0
174351 | BUS-3 | TL_3-4 | Line | -22.922 | 7.597 | 0.2 | -174.4 | 0 |  |  | 0.4027 | -2.5029 |  | 0 | 0 |  |  | %/Ohm: 0
174351 | BUS-4 | TL_3-4 | Line | 23.325 | -10.1 | 0.21 | 13.2 | 0 |  |  | 0.4027 | -2.5029 |  | 0 | 0 |  |  | %/Ohm: 0
174371 | BUS-4 | TL_2-4 | Line | -54.409 | -1.333 | 0.451 | 168.4 | 0 |  |  | 1.6853 | 1.1627 |  | 0 | 0 |  |  | %/Ohm: 0
174371 | BUS-2 | TL_2-4 | Line | 56.094 | 2.496 | 0.45 | -7.5 | 0 |  |  | 1.6853 | 1.1627 |  | 0 | 0 |  |  | %/Ohm: 0
174366 | BUS-4 | TL_5-4 | Line | -62.018 | 2.18 | 0.514 | 171.8 | 0 |  |  | 0.504 | 0.2737 |  | 0 | 0 |  |  | %/Ohm: 0
174391 | BUS-13 | LDBUS_13 | Load | 13.5 | 5.8 | 0.616 | -39 | 0 | 1 | 1
174382 | BUS-11 | LDBUS_11 | Load | 3.5 | 1.8 | 0.164 | -42.5 | 0 | 1 | 1
174412 | BUS-5 | LDBUS_5 | Load | 7.6 | 1.6 | 0.064 | -20.6 | 0 | 1 | 1
174403 | BUS-3 | LDBUS_3 | Load | 94.2 | 19 | 0.796 | -24.2 | 0 | 1 | 1
174128 | BUS-1 | SL_GEN_bus_1 | Network Feeder | 0 | 0 | 0 | 0 | 0
174421 | BUS-2 | LDBUS_2 | Load | 21.7 | 12.7 | 0.201 | -35.3 | 0 | 1 | 1
174141 | BUS-2 | GEN_bus_2 | Synchronous Machine | -40 | -48.794 | 0.505 | 124.4 | 0 | 1 | 1
174439 | BUS-4 | LDBUS_4 | Load | 47.8 | 4 | 0.397 | -15 | 0 | 1 | 1
174430 | BUS-6 | LDBUS_6 | Load | 11.2 | 7.5 | 0.554 | -48.6 | 0 | 1 | 1
174151 | BUS-6 | SYN_COND_bus_6 | Synchronous Machine | 0 | -24 | 0.986 | 75.3 | 0 | 1 | 1
174457 | BUS-12 | LDBUS_12 | Load | 6.1 | 1.6 | 0.263 | -30.4 | 0 | 1 | 1
174448 | BUS-14 | LDBUS_14 | Load | 14.9 | 5 | 0.67 | -35.2 | 0 | 1 | 1
174175 | BUS-3 | SYN_CON_bus_3 | Synchronous Machine | 0 | -28.34 | 0.235 | 77.2 | 0 | 1 | 1
174185 | BUS-8 | SYN_CON_bus_8 | Synchronous Machine | 0 | -24 | 0.721 | 76.5 | 0 | 1 | 1
174475 | BUS-9 | LDBUS_9 | Load | 29.5 | 16.6 | 1.412 | -44.7 | 0 | 1 | 1
174466 | BUS-10 | LDBUS_10 | Load | 9 | 5.8 | 0.449 | -48.3 | 0 | 1 | 1
174486 | BUS-1 | SL_GEN_1 | Synchronous Machine | -232.501 | 15.762 | 1.84 | -176.1 | 0 | 1 | 1
174216 | BUS-5 | Xmer_5-6 | 2W Transformer | 42.986 | 2.092 | 0.354 | -11.5 | 0 |  |  | 0 | 4.5069 | 0 |  |  | 0 |  | %/Ohm: 0
174216 | BUS-6 | Xmer_5-6 | 2W Transformer | -42.986 | 2.415 | 1.769 | 168.5 | 0 |  |  | 0 | 4.5069 | 0 |  |  | 0 |  | %/Ohm: 0
174230 | BUS-4 | TRF_4-9 | 2W Transformer | 16.119 | 2.115 | 0.135 | -17.7 | 0 |  |  | 0 | 1.4399 | 0 |  |  | 0 |  | %/Ohm: 0
174230 | BUS-9 | TRF_4-9 | 2W Transformer | -16.119 | -0.675 | 0.673 | 162.3 | 0 |  |  | 0 | 1.4399 | 0 |  |  | 0 |  | %/Ohm: 0
174257 | BUS-7 | TRF_7-8 | 2W Transformer | 0 | -23.11 | 0.94 | 76.5 | 0 |  |  | 0 | 0.8895 | 0 |  |  | 0 |  | %/Ohm: 0
174257 | BUS-8 | TRF_7-8 | 2W Transformer | 0 | 24 | 0.721 | -103.5 | 0 |  |  | 0 | 0.8895 | 0 |  |  | 0 |  | %/Ohm: 0
174283 | BUS-5 | TL_2-5 | Line | -40.511 | -3.152 | 0.334 | 166.8 | 0 |  |  | 0.9034 | -0.8588 |  | 0 | 0 |  |  | %/Ohm: 0
174283 | BUS-2 | TL_2-5 | Line | 41.414 | 2.293 | 0.332 | -8.2 | 0 |  |  | 0.9034 | -0.8588 |  | 0 | 0 |  |  | %/Ohm: 0
174271 | BUS-4 | TRF_4-7 | 2W Transformer | 29.183 | 3.138 | 0.243 | -16.4 | 0 |  |  | 0 | 1.688 | 0 |  |  | 0 |  | %/Ohm: 0
174271 | BUS-7 | TRF_4-7 | 2W Transformer | -29.183 | -1.45 | 1.189 | 163.6 | 0 |  |  | 0 | 1.688 | 0 |  |  | 0 |  | %/Ohm: 0
174298 | BUS-6 | TL_6-13 | Line | 17.417 | 7.485 | 0.779 | -38 | 0 |  |  | 0.2293 | 0.4516 |  | 0 | 0 |  |  | %/Ohm: 0
174298 | BUS-13 | TL_6-13 | Line | -17.187 | -7.033 | 0.779 | 142 | 0 |  |  | 0.2293 | 0.4516 |  | 0 | 0 |  |  | %/Ohm: 0
174293 | BUS-12 | TL_12-13 | Line | 1.539 | 0.829 | 0.073 | -44 | 0 |  |  | 0.0067 | 0.0061 |  | 0 | 0 |  |  | %/Ohm: 0
174293 | BUS-13 | TL_12-13 | Line | -1.532 | -0.822 | 0.073 | 136 | 0 |  |  | 0.0067 | 0.0061 |  | 0 | 0 |  |  | %/Ohm: 0
174288 | BUS-6 | TL_6-12 | Line | 7.717 | 2.592 | 0.335 | -33.3 | 0 |  |  | 0.0786 | 0.1636 |  | 0 | 0 |  |  | %/Ohm: 0
174288 | BUS-12 | TL_6-12 | Line | -7.639 | -2.429 | 0.335 | 146.7 | 0 |  |  | 0.0786 | 0.1636 |  | 0 | 0 |  |  | %/Ohm: 0
174318 | BUS-14 | TL_9-14 | Line | -9.735 | -3.055 | 0.435 | 146 | 0 |  |  | 0.1374 | 0.2922 |  | 0 | 0 |  |  | %/Ohm: 0
174313 | BUS-9 | TL_9-10 | Line | 5.93 | 3.776 | 0.293 | -47.8 | 0 |  |  | 0.0156 | 0.0415 |  | 0 | 0 |  |  | %/Ohm: 0
174313 | BUS-10 | TL_9-10 | Line | -5.914 | -3.734 | 0.293 | 132.2 | 0 |  |  | 0.0156 | 0.0415 |  | 0 | 0 |  |  | %/Ohm: 0
174308 | BUS-11 | TL_11-10 | Line | 3.097 | 2.093 | 0.156 | -49.3 | 0 |  |  | 0.0114 | 0.0266 |  | 0 | 0 |  |  | %/Ohm: 0
174308 | BUS-10 | TL_11-10 | Line | -3.086 | -2.066 | 0.156 | 130.7 | 0 |  |  | 0.0114 | 0.0266 |  | 0 | 0 |  |  | %/Ohm: 0
174303 | BUS-6 | TL_6-11 | Line | 6.652 | 4.008 | 0.319 | -45.8 | 0 |  |  | 0.0553 | 0.1157 |  | 0 | 0 |  |  | %/Ohm: 0
174303 | BUS-11 | TL_6-11 | Line | -6.597 | -3.893 | 0.319 | 134.2 | 0 |  |  | 0.0553 | 0.1157 |  | 0 | 0 |  |  | %/Ohm: 0
174331 | BUS-9 | TL_7-9 | Line | -29.183 | -23.047 | 1.552 | 126.4 | 0 |  |  | 0 | 1.5132 |  | 0 | 0 |  |  | %/Ohm: 0
174331 | BUS-7 | TL_7-9 | Line | 29.183 | 24.56 | 1.552 | -53.6 | 0 |  |  | 0 | 1.5132 |  | 0 | 0 |  |  | %/Ohm: 0
174323 | BUS-14 | TL_14-13 | Line | -5.165 | -1.945 | 0.235 | 142.8 | 0 |  |  | 0.0541 | 0.1101 |  | 0 | 0 |  |  | %/Ohm: 0
174323 | BUS-13 | TL_14-13 | Line | 5.22 | 2.055 | 0.235 | -37.2 | 0 |  |  | 0.0541 | 0.1101 |  | 0 | 0 |  |  | %/Ohm: 0
174318 | BUS-9 | TL_9-14 | Line | 9.872 | 3.347 | 0.435 | -34 | 0 |  |  | 0.1374 | 0.2922 |  | 0 | 0 |  |  | %/Ohm: 0
174346 | BUS-3 | TL_3-2 | Line | -71.278 | 1.743 | 0.591 | 168.6 | 0 |  |  | 2.3476 | 5.265 |  | 0 | 0 |  |  | %/Ohm: 0
174346 | BUS-2 | TL_3-2 | Line | 73.626 | 3.522 | 0.59 | -7.7 | 0 |  |  | 2.3476 | 5.265 |  | 0 | 0 |  |  | %/Ohm: 0
174336 | BUS-2 | TL_1-2 | Line | -152.834 | 27.782 | 1.244 | -174.7 | 0 |  |  | 4.3122 | 7.3166 |  | 0 | 0 |  |  | %/Ohm: 0
174336 | BUS-1 | TL_1-2 | Line | 157.146 | -20.466 | 1.251 | 7.4 | 0 |  |  | 4.3122 | 7.3166 |  | 0 | 0 |  |  | %/Ohm: 0

## Node Results
Bus Data Summary
ID | Name | U (kV) | u (%) | U ang (°) | P Load (MW) | Q Load (MVAr) | P Gen (MW) | Q Gen (MVAr) | Q Shunt (MVAr) | Sens. PG/Nodal | Sens. QG | DU Feeder | Description | Zone | Area | Partial Network | Feeder
174092 | BUS-1 | 73.14 | 106 | 0 | 15.762 | 0 | 232.501 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174077 | BUS-10 | 13.767 | 99.76 | -15.5 | 5.9 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174074 | BUS-11 | 13.857 | 100.41 | -15.3 | 5.3 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174075 | BUS-12 | 13.833 | 100.24 | -15.7 | 5.7 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174061 | BUS-13 | 13.764 | 99.96 | -15.7 | 13.5 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174063 | BUS-14 | 13.545 | 98.14 | -16.6 | 14.9 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174062 | BUS-15 | 72.105 | 104.5 | -12.7 | 12.7 | 4 | 0 | 48.794 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174096 | BUS-3 | 69.696 | 101.12 | -12.8 | 94.2 | 19 | 0 | 28.34 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174095 | BUS-4 | 69.715 | 101.04 | -12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174090 | BUS-5 | 70.222 | 101.77 | -8.7 | 2.6 | 1.6 | 0 | 24 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174093 | BUS-6 | 45.01 | 101.1 | -14.7 | 1.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174082 | BUS-7 | 14.192 | 102.84 | -13.4 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174081 | BUS-8 | 13.804 | 100.6 | -15.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1
174071 | BUS-9 | 13.837 | 100.26 | -15.3 | 29.5 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | Zone 1 | Area 1 | 1

## Element Results
ID | Node Name | Element | Type | P (MW) | Q (MW) | I (kA) | Angle I | Loading % | P loss (MW) | Q loss (MVAR) | P Fe (MW) | Q Com Mvar | Tap | Sens. Xser %Ohm | On | Description | Zone 1 | Area 1 | Partial | Feeder
174361 | BUS-1 | TL_1-5 | Line | 75.355 | 4.704 | 0.596 | -3.6 | 0 | 2.7573 | 6.0706 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174128 | BUS-1 | SL_GEN_bus_1 | Network Feeder | 0 | 0 | 0 | 0 | [7 empty] | OFF |  | Zone 1 | Area 1 | -1
174486 | BUS-1 | SL_GEN_1 | Synchronous Machine | -232.501 | 15.762 | 1.84 | -176.1 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174336 | BUS-1 | TL_1-2 | Line | 157.146 | -20.466 | 1.251 | 7.4 | 0 | 4.3122 | 7.3166 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174466 | BUS-10 | LDBUS_10 | Load | 9 | 5.8 | 0.449 | -48.3 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174313 | BUS-10 | TL_9-10 | Line | -5.914 | -3.734 | 0.293 | 132.2 | 0 | 0.0156 | 0.0415 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174308 | BUS-10 | TL_11-10 | Line | -3.086 | -2.066 | 0.156 | 130.7 | 0 | 0.0114 | 0.0266 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174382 | BUS-11 | LDBUS_11 | Load | 3.5 | 1.8 | 0.164 | -42.5 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174308 | BUS-11 | TL_11-10 | Line | 3.097 | 2.093 | 0.156 | -49.3 | 0 | 0.0114 | 0.0266 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174303 | BUS-11 | TL_6-11 | Line | -6.597 | -3.893 | 0.319 | 134.2 | 0 | 0.0553 | 0.1157 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174457 | BUS-12 | LDBUS_12 | Load | 6.1 | 1.6 | 0.263 | -30.4 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174293 | BUS-12 | TL_12-13 | Line | 1.539 | 0.829 | 0.073 | -44 | 0 | 0.0067 | 0.0061 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174288 | BUS-12 | TL_6-12 | Line | -7.639 | -2.429 | 0.335 | 146.7 | 0 | 0.0786 | 0.1636 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174391 | BUS-13 | LDBUS_13 | Load | 13.5 | 5.8 | 0.616 | -39 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174298 | BUS-13 | TL_6-13 | Line | -17.187 | -7.033 | 0.779 | 142 | 0 | 0.2293 | 0.4516 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174293 | BUS-13 | TL_12-13 | Line | -1.532 | -0.822 | 0.073 | 136 | 0 | 0.0067 | 0.0061 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174323 | BUS-13 | TL_14-13 | Line | 5.22 | 2.055 | 0.235 | -37.2 | 0 | 0.0541 | 0.1101 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174448 | BUS-14 | LDBUS_14 | Load | 14.9 | 5 | 0.67 | -35.2 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174318 | BUS-14 | TL_9-14 | Line | -9.735 | -3.055 | 0.435 | 146 | 0 | 0.1374 | 0.2922 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174323 | BUS-14 | TL_14-13 | Line | -5.165 | -1.945 | 0.235 | 142.8 | 0 | 0.0541 | 0.1101 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174371 | BUS-2 | TL_2-4 | Line | 56.094 | 2.496 | 0.45 | -7.5 | 0 | 1.6853 | 1.1627 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174421 | BUS-2 | LDBUS_2 | Load | 21.7 | 12.7 | 0.201 | -35.3 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174141 | BUS-2 | GEN_bus_2 | Synchronous Machine | -40 | -48.794 | 0.505 | 124.4 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174283 | BUS-2 | TL_2-5 | Line | 41.414 | 2.293 | 0.332 | -8.2 | 0 | 0.9034 | -0.8588 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174346 | BUS-2 | TL_3-2 | Line | 73.626 | 3.522 | 0.59 | -7.7 | 0 | 2.3476 | 5.265 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174336 | BUS-2 | TL_1-2 | Line | -152.834 | 27.782 | 1.244 | -174.7 | 0 | 4.3122 | 7.3166 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174351 | BUS-3 | TL_3-4 | Line | -22.922 | 7.597 | 0.2 | -174.4 | 0 | 0.4027 | -2.5029 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174403 | BUS-3 | LDBUS_3 | Load | 94.2 | 19 | 0.796 | -24.2 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174175 | BUS-3 | SYN_CON_bus_3 | Synchronous Machine | 0 | -28.34 | 0.235 | 77.2 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174346 | BUS-3 | TL_3-2 | Line | -71.278 | 1.743 | 0.591 | 168.6 | 0 | 2.3476 | 5.265 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174351 | BUS-4 | TL_3-4 | Line | 23.325 | -10.1 | 0.21 | 13.2 | 0 | 0.4027 | -2.5029 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174371 | BUS-4 | TL_2-4 | Line | -54.409 | -1.333 | 0.451 | 168.4 | 0 | 1.6853 | 1.1627 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174366 | BUS-4 | TL_5-4 | Line | -62.018 | 2.18 | 0.514 | 171.8 | 0 | 0.504 | 0.2737 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174439 | BUS-4 | LDBUS_4 | Load | 47.8 | 4 | 0.397 | -15 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174230 | BUS-4 | TRF_4-9 | 2W Transformer | 16.119 | 2.115 | 0.135 | -17.7 | 0 | 0 | 1.4399 | 0 |  | 0 | 0 | ON |  | Zone 1 | Area 1 | 1
174271 | BUS-4 | TRF_4-7 | 2W Transformer | 29.183 | 3.138 | 0.243 | -16.4 | 0 | 0 | 1.688 | 0 |  | 0 | 0 | ON |  | Zone 1 | Area 1 | 1
174366 | BUS-5 | TL_5-4 | Line | 62.522 | -1.906 | 0.514 | -7 | 0 | 0.504 | 0.2737 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174361 | BUS-5 | TL_1-5 | Line | -72.598 | 1.366 | 0.597 | 172.3 | 0 | 2.7573 | 6.0706 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174412 | BUS-5 | LDBUS_5 | Load | 7.6 | 1.6 | 0.064 | -20.6 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174216 | BUS-5 | Xmer_5-6 | 2W Transformer | 42.986 | 2.092 | 0.354 | -11.5 | 0 | 0 | 4.5069 | 0 |  | 0 | 0 | ON |  | Zone 1 | Area 1 | 1
174283 | BUS-5 | TL_2-5 | Line | -40.511 | -3.152 | 0.334 | 166.8 | 0 | 0.9034 | -0.8588 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174430 | BUS-6 | LDBUS_6 | Load | 11.2 | 7.5 | 0.554 | -48.6 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174151 | BUS-6 | SYN_COND_bus_6 | Synchronous Machine | 0 | -24 | 0.986 | 75.3 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174216 | BUS-6 | Xmer_5-6 | 2W Transformer | -42.986 | 2.415 | 1.769 | 168.5 | 0 | 0 | 4.5069 | 0 |  | 0 | 0 | ON |  | Zone 1 | Area 1 | 1
174298 | BUS-6 | TL_6-13 | Line | 17.417 | 7.485 | 0.779 | -38 | 0 | 0.2293 | 0.4516 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174288 | BUS-6 | TL_6-12 | Line | 7.717 | 2.592 | 0.335 | -33.3 | 0 | 0.0786 | 0.1636 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174303 | BUS-6 | TL_6-11 | Line | 6.652 | 4.008 | 0.319 | -45.8 | 0 | 0.0553 | 0.1157 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174257 | BUS-7 | TRF_7-8 | 2W Transformer | 0 | -23.11 | 0.94 | 76.5 | 0 | 0 | 0.8895 | 0 |  | 0 | 0 | ON |  | Zone 1 | Area 1 | 1
174271 | BUS-7 | TRF_4-7 | 2W Transformer | -29.183 | -1.45 | 1.189 | 163.6 | 0 | 0 | 1.688 | 0 |  | 0 | 0 | ON |  | Zone 1 | Area 1 | 1
174331 | BUS-7 | TL_7-9 | Line | 29.183 | 24.56 | 1.552 | -53.6 | 0 | 0 | 1.5132 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174185 | BUS-8 | SYN_CON_bus_8 | Synchronous Machine | 0 | -24 | 0.721 | 76.5 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174257 | BUS-8 | TRF_7-8 | 2W Transformer | 0 | 24 | 0.721 | -103.5 | 0 | 0 | 0.8895 | 0 |  | 0 | 0 | ON |  | Zone 1 | Area 1 | 1
174475 | BUS-9 | LDBUS_9 | Load | 29.5 | 16.6 | 1.412 | -44.7 | [7 empty] | ON |  | Zone 1 | Area 1 | 1
174230 | BUS-9 | TRF_4-9 | 2W Transformer | -16.119 | -0.675 | 0.673 | 162.3 | 0 | 0 | 1.4399 | 0 |  | 0 | 0 | ON |  | Zone 1 | Area 1 | 1
174313 | BUS-9 | TL_9-10 | Line | 5.93 | 3.776 | 0.293 | -47.8 | 0 | 0.0156 | 0.0415 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174331 | BUS-9 | TL_7-9 | Line | -29.183 | -23.047 | 1.552 | 126.4 | 0 | 0 | 1.5132 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1
174318 | BUS-9 | TL_9-14 | Line | 9.872 | 3.347 | 0.435 | -34 | 0 | 0.1374 | 0.2922 |  | 0 |  | 0 | ON |  | Zone 1 | Area 1 | 1

## Element Results (Detailed)
|  | Element Name | Type | P (MW) | Q(Mvar) | I(kA) | Angle I | Loading % | Scaling P | Scaling Q | P loss (MW) | Q loss (Mvar) | P Fe (MW) | P Comp MW | Q comp (Mvar) | Tap | Ratio | Sens. Xser %Ohm | Theta
174361 | BUS-1 | TL_1-5 | Line | 75.355 | 4.704 | 0.596 | -3.6 | 0 |  |  | 2.7573 | 6.0706 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174128 | BUS-1 | SL_GEN_bus_1 | Network Feeder | 0 | 0 | 0 | 0 | 0 | [11 empty] | OFF | Zone 1 | Area 1 | -1
174486 | BUS-1 | SL_GEN_1 | Synchronous Machine | -232.501 | 15.762 | 1.84 | -176.1 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174336 | BUS-1 | TL_1-2 | Line | 157.146 | -20.466 | 1.251 | 7.4 | 0 |  |  | 4.3122 | 7.3166 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174466 | BUS-10 | LDBUS_10 | Load | 9 | 5.8 | 0.449 | -48.3 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174313 | BUS-10 | TL_9-10 | Line | -5.914 | -3.734 | 0.293 | 132.2 | 0 |  |  | 0.0156 | 0.0415 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174308 | BUS-10 | TL_11-10 | Line | -3.086 | -2.066 | 0.156 | 130.7 | 0 |  |  | 0.0114 | 0.0266 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174382 | BUS-11 | LDBUS_11 | Load | 3.5 | 1.8 | 0.164 | -42.5 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174308 | BUS-11 | TL_11-10 | Line | 3.097 | 2.093 | 0.156 | -49.3 | 0 |  |  | 0.0114 | 0.0266 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174303 | BUS-11 | TL_6-11 | Line | -6.597 | -3.893 | 0.319 | 134.2 | 0 |  |  | 0.0553 | 0.1157 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174457 | BUS-12 | LDBUS_12 | Load | 6.1 | 1.6 | 0.263 | -30.4 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174293 | BUS-12 | TL_12-13 | Line | 1.539 | 0.829 | 0.073 | -44 | 0 |  |  | 0.0067 | 0.0061 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174288 | BUS-12 | TL_6-12 | Line | -7.639 | -2.429 | 0.335 | 146.7 | 0 |  |  | 0.0786 | 0.1636 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174391 | BUS-13 | LDBUS_13 | Load | 13.5 | 5.8 | 0.616 | -39 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174298 | BUS-13 | TL_6-13 | Line | -17.187 | -7.033 | 0.779 | 142 | 0 |  |  | 0.2293 | 0.4516 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174293 | BUS-13 | TL_12-13 | Line | -1.532 | -0.822 | 0.073 | 136 | 0 |  |  | 0.0067 | 0.0061 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174323 | BUS-13 | TL_14-13 | Line | 5.22 | 2.055 | 0.235 | -37.2 | 0 |  |  | 0.0541 | 0.1101 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174448 | BUS-14 | LDBUS_14 | Load | 14.9 | 5 | 0.67 | -35.2 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174318 | BUS-14 | TL_9-14 | Line | -9.735 | -3.055 | 0.435 | 146 | 0 |  |  | 0.1374 | 0.2922 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174323 | BUS-14 | TL_14-13 | Line | -5.165 | -1.945 | 0.235 | 142.8 | 0 |  |  | 0.0541 | 0.1101 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174371 | BUS-2 | TL_2-4 | Line | 56.094 | 2.496 | 0.45 | -7.5 | 0 |  |  | 1.6853 | 1.1627 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174421 | BUS-2 | LDBUS_2 | Load | 21.7 | 12.7 | 0.201 | -35.3 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174141 | BUS-2 | GEN_bus_2 | Synchronous Machine | -40 | -48.794 | 0.505 | 124.4 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174283 | BUS-2 | TL_2-5 | Line | 41.414 | 2.293 | 0.332 | -8.2 | 0 |  |  | 0.9034 | -0.8588 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174346 | BUS-2 | TL_3-2 | Line | 73.626 | 3.522 | 0.59 | -7.7 | 0 |  |  | 2.3476 | 5.265 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174336 | BUS-2 | TL_1-2 | Line | -152.834 | 27.782 | 1.244 | -174.7 | 0 |  |  | 4.3122 | 7.3166 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174351 | BUS-3 | TL_3-4 | Line | -22.922 | 7.597 | 0.2 | -174.4 | 0 |  |  | 0.4027 | -2.5029 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174403 | BUS-3 | LDBUS_3 | Load | 94.2 | 19 | 0.796 | -24.2 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174175 | BUS-3 | SYN_CON_bus_3 | Synchronous Machine | 0 | -28.34 | 0.235 | 77.2 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174346 | BUS-3 | TL_3-2 | Line | -71.278 | 1.743 | 0.591 | 168.6 | 0 |  |  | 2.3476 | 5.265 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174351 | BUS-4 | TL_3-4 | Line | 23.325 | -10.1 | 0.21 | 13.2 | 0 |  |  | 0.4027 | -2.5029 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174371 | BUS-4 | TL_2-4 | Line | -54.409 | -1.333 | 0.451 | 168.4 | 0 |  |  | 1.6853 | 1.1627 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174366 | BUS-4 | TL_5-4 | Line | -62.018 | 2.18 | 0.514 | 171.8 | 0 |  |  | 0.504 | 0.2737 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174439 | BUS-4 | LDBUS_4 | Load | 47.8 | 4 | 0.397 | -15 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174230 | BUS-4 | TRF_4-9 | 2W Transformer | 16.119 | 2.115 | 0.135 | -17.7 | 0 |  |  | 0 | 1.4399 | 0 |  |  | 0 |  | 0 |  | ON | Zone 1 | Area 1 | 1
174271 | BUS-4 | TRF_4-7 | 2W Transformer | 29.183 | 3.138 | 0.243 | -16.4 | 0 |  |  | 0 | 1.688 | 0 |  |  | 0 |  | 0 |  | ON | Zone 1 | Area 1 | 1
174366 | BUS-5 | TL_5-4 | Line | 62.522 | -1.906 | 0.514 | -7 | 0 |  |  | 0.504 | 0.2737 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174361 | BUS-5 | TL_1-5 | Line | -72.598 | 1.366 | 0.597 | 172.3 | 0 |  |  | 2.7573 | 6.0706 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174412 | BUS-5 | LDBUS_5 | Load | 7.6 | 1.6 | 0.064 | -20.6 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174216 | BUS-5 | Xmer_5-6 | 2W Transformer | 42.986 | 2.092 | 0.354 | -11.5 | 0 |  |  | 0 | 4.5069 | 0 |  |  | 0 |  | 0 |  | ON | Zone 1 | Area 1 | 1
174283 | BUS-5 | TL_2-5 | Line | -40.511 | -3.152 | 0.334 | 166.8 | 0 |  |  | 0.9034 | -0.8588 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174430 | BUS-6 | LDBUS_6 | Load | 11.2 | 7.5 | 0.554 | -48.6 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174151 | BUS-6 | SYN_COND_bus_6 | Synchronous Machine | 0 | -24 | 0.986 | 75.3 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174216 | BUS-6 | Xmer_5-6 | 2W Transformer | -42.986 | 2.415 | 1.769 | 168.5 | 0 |  |  | 0 | 4.5069 | 0 |  |  | 0 |  | 0 |  | ON | Zone 1 | Area 1 | 1
174298 | BUS-6 | TL_6-13 | Line | 17.417 | 7.485 | 0.779 | -38 | 0 |  |  | 0.2293 | 0.4516 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174288 | BUS-6 | TL_6-12 | Line | 7.717 | 2.592 | 0.335 | -33.3 | 0 |  |  | 0.0786 | 0.1636 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174303 | BUS-6 | TL_6-11 | Line | 6.652 | 4.008 | 0.319 | -45.8 | 0 |  |  | 0.0553 | 0.1157 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174257 | BUS-7 | TRF_7-8 | 2W Transformer | 0 | -23.11 | 0.94 | 76.5 | 0 |  |  | 0 | 0.8895 | 0 |  |  | 0 |  | 0 |  | ON | Zone 1 | Area 1 | 1
174271 | BUS-7 | TRF_4-7 | 2W Transformer | -29.183 | -1.45 | 1.189 | 163.6 | 0 |  |  | 0 | 1.688 | 0 |  |  | 0 |  | 0 |  | ON | Zone 1 | Area 1 | 1
174331 | BUS-7 | TL_7-9 | Line | 29.183 | 24.56 | 1.552 | -53.6 | 0 |  |  | 0 | 1.5132 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174185 | BUS-8 | SYN_CON_bus_8 | Synchronous Machine | 0 | -24 | 0.721 | 76.5 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174257 | BUS-8 | TRF_7-8 | 2W Transformer | 0 | 24 | 0.721 | -103.5 | 0 |  |  | 0 | 0.8895 | 0 |  |  | 0 |  | 0 |  | ON | Zone 1 | Area 1 | 1
174475 | BUS-9 | LDBUS_9 | Load | 29.5 | 16.6 | 1.412 | -44.7 | 0 | 1 | 1 | [9 empty] | ON | Zone 1 | Area 1 | 1
174230 | BUS-9 | TRF_4-9 | 2W Transformer | -16.119 | -0.675 | 0.673 | 162.3 | 0 |  |  | 0 | 1.4399 | 0 |  |  | 0 |  | 0 |  | ON | Zone 1 | Area 1 | 1
174313 | BUS-9 | TL_9-10 | Line | 5.93 | 3.776 | 0.293 | -47.8 | 0 |  |  | 0.0156 | 0.0415 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174331 | BUS-9 | TL_7-9 | Line | -29.183 | -23.047 | 1.552 | 126.4 | 0 |  |  | 0 | 1.5132 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1
174318 | BUS-9 | TL_9-14 | Line | 9.872 | 3.347 | 0.435 | -34 | 0 |  |  | 0.1374 | 0.2922 |  | 0 | 0 |  |  | 0 |  | ON | Zone 1 | Area 1 | 1

## Summary
From Area/Zone | To Area/Zone | P Loss (MW) | Q Loss (MVAr) | P Imp (MW) | Q Imp (MVAr) | P Gen (MW) | Q Gen (MVAr) | P Load (MW) | Q Load (MVAr) | Gen. Cost (Curr. Units) | Qc Shunt (MVAr) | Ql Shunt (MVAr) | Q Comp (MVAr) | Iron Losses (MW)
Network |  | 13.501 | 27.972 | 232.501 | -15.762 | 272.501 | 33.032 | 259 | 5.06 | 0 | 0 | 0 | 0 | 0
Area 1 |  | 13.501 | 27.972 | 0 | 0 | 272.501 | 33.032 | 259 | 5.06 | 0 | 0 | 0 | 0 | 0
Zone 1 |  | 13.501 | 27.972 | 0 | 0 | 272.501 | 33.032 | 259 | 5.06 | 0 | 0 | 0 | 0 | 0
Voltage (kV) | P Loss Li (MW) | Q Loss Li (MVAr) | P Loss L (MW) | Q Loss L (MVAr) | P Loss T (MW) | Q Loss T (MVAr)
7.8 | 0.588 | 2.721 | 0 | 0 | 0 | 0
13.8 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0.89 | 0
69 | 12.913 | 16.727 | 0 | 0 | 7.635 | 0

## Conclusions
positive value means generating
negative value means consuming