## Short Circuit Analysis
Cos(Phi) = 0.9 assumed for all synchronous machines
Fault Current
ID | Fault Location From | To Node | Distance from fault | Element Name | Type | Un (kV) | UL-E (kV) | AU L-E (°) | Ik'' (kA) | AIk'' (°) | Fault Type | Method | Maximum | Network Type | CB Delay Time (s) | SC Duration (s) | SC Duration (s) | Zone | Area | Partial Network | Feeder
174086 | BUS-4 | Faulted | 0 | — | — | 69 | 43.82 | 180 | 12.717 | -81.38 | 3phase | IEC6090 | ☑ | MESHED | 0.02 | 1 | 0.02 | Zone 1 | Area 1 | 1
174351 | BUS-4 | BUS-3 | — | TL_3-4 | Line | — | 2.828 | 103.55 | — | — | — | — | ☐ | — | — | — | — | Zone 1 | Area 1 | 1
174366 | BUS-4 | BUS-5 | — | TL_5-4 | Line | — | 4.573 | 97.52 | — | — | — | — | ☐ | — | — | — | — | Zone 1 | Area 1 | 1
174371 | BUS-4 | BUS-2 | — | TL_2-4 | Line | — | 2.563 | 100.69 | — | — | — | — | ☐ | — | — | — | — | Zone 1 | Area 1 | 1
174230 | BUS-4 | BUS-9 | — | TRF_4-9 | 2W Transfo | — | 0.808 | 95.12 | — | — | — | — | ☐ | — | — | — | — | Zone 1 | Area 1 | 1
174271 | BUS-4 | BUS-7 | — | TRF_4-7 | 2W Transfo | — | 1.97 | 92.84 | — | — | — | — | ☐ | — | — | — | — | Zone 1 | Area 1 | 1
Current at fault locations
ID | Fault Location | Un (kV) | Ik''(kA) | AIk'' (°) | Fault Type | Method | Maximum | Network Type | CB Delay Time (s) | SC Duration (s) | SC Duration (s) | Description | Zone | Area | Partial Network | Feeder
174086 | BUS-4 | 69 | 12.71 | -81.38 | 3phase fault | IEC60909 | ☑ | MESHED | 0.02 | 1 | 0.02 | — | Zone 1 | Area 1 | 1
Node Voltages
ID | Name | Faulted | Un (kV) | U L-E (kV) | AU L-E (°) | U L-L (kV) | AU L-L (°) | U (012) (kV) | AU (012) (°) | U0 (kV) | AU0 (°) | Fault Type | Method | Maximum | Description | Zone | Area | Partial Network | Feeder
174086 | BUS-4 | ☑ | 69 | 43.821 | 180 | 75.9 | 330 | 43.821 | 180 | 0 | -90 | 3phase fault | IEC60909 | ☑ | — | Zone 1 | Area 1 | 1